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IT IS ABSOLUTELY ESSENTIAL TO
PROVIDE CLOSE SUPERVISION DURING
SYSTEM IMPAIRMENTS

 Notify Marsh well in advance of impairment. 
In emergency, contact your local Marsh representative:
Ken. E Botes (Atlanta, GA)
Mobile: 404 216 3425
Email: Ken.Botes@marsh.com

 Contact the central station monitoring company.
 Notify public fire department of impairment.
 Shut down hazardous operations until protection is restored.
 Provide temporary protection. Move extra extinguishers to area involved. Lay out charged fire hose lines.
 Provide standby personnel with emergency instructions.
 During impairment, building or areas involved should be constantly attended.
 Upon completion of repairs or alterations, check to assure all valves are open and all systems operative. Then notify Marsh Risk Consulting of restoration.
 A main drain (2 in. drain) test is required after reopening a valve on a riser. 
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ATTACH TO VALVE
* READ INSTRUCTIONS ON OTHER SIDE *
FIRE PROTECTION SYSTEM
IMPAIRMENT

	THIS SYSTEM PROTECTS:

	

	DATE / TIME SHUT
	SHUT BY

	
	



For sprinkler systems, after valve is opened, make 2” drain test.
Drop in pressure should be normal. If pressure drop is extreme and does not build up, the system is impaired and immediate investigation is necessary.

	MANDATORY DRAIN TEST RESULTS

	STATIC PRESSURE
	FLOWING PRESSURE

	
	

	DRAIN TEST MADE BY
	DATE / TIME OPENED
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