Lightning protection inspection checklist

Based on NFPA 780, Annex D. This is a practical inspection checklist; the applicable adopted edition and the authority having jurisdiction should be confirmed.

Inspection frequency

- Conduct a visual inspection at least annually.

- Consider semiannual inspections, or an inspection after extreme temperature changes, where severe climatic changes occur.

- Complete an in-depth inspection every 3–5 years.

- Inspect critical systems every 1–3 years, depending on occupancy and environment.

Visual inspection

- System is in good repair.

- No loose connections that could create high-resistance joints.

- No component is weakened by corrosion or vibration.

- Down conductors and grounding electrodes are intact and not severed.

- Conductors and components are securely fastened to their mounting surfaces and protected from accidental mechanical displacement.

- No building additions or alterations require additional lightning protection.

- Surge protective devices (SPDs) show no visible damage.

- SPD status lights, where provided, are functioning.

- System complies with the applicable current edition of NFPA 780.

Maintenance and testing

- Inspect all conductors and system components.

- Tighten clamps and splicers.

- Measure lightning protection system resistance.

- Measure grounding-electrode resistance.

- Inspect or test surge-protection equipment to evaluate its effectiveness.

- Refasten or tighten components and conductors as needed.

- Evaluate whether structural additions or changes have reduced system effectiveness.

Complete inspection and testing

- Test continuity of concealed portions that cannot be visually inspected.

- Test grounding-electrode termination systems and individual grounding electrodes where suitable disconnecting means are provided.

- Compare grounding results with prior/original results or accepted values for the soil conditions.

- Test continuity to verify equipotential bonding for new interior services or construction.

Documentation

- Record installation methods, component types and conditions, test methods, and test data on an inspection form or guide.

- Keep inspection and maintenance records available to the responsible inspection authority.